## PC Version
INPUT DATA
Ambient Condition |  |  | Gas Composition
Barometric Pressure | 14.663 | Psia | CH4 | Methane | 91.026 | % | UTis
Inlet Dry Bulb Temperature | 88.682 | F | C2H6 | Ethane | 6.533 | %
Inlet Wet Bulb Temperature | 0 | F | C3H8 | Propane | 1.1 | %
Inlet Relative Humidity | 88.83 | % | i-C4H10 | I-Butane | 0.081 | %
|  |  | n-C4H10 | N-Butane | 0.08 | % | GAS TURBINE EXHAUST CALCULATION
Gas Turbine |  |  | i-C5H12 | I-Petane | 0.027 | %
GT Fuel Flow | 77382.25 | lb/hr | n-C5H12 | N-Petane | 0.022 | %
Fuel Temperature | 80.6 | F | C6H14 | Hexane | 0 | %
|  |  | N2 | Nitrogen | 0.499 | %
Injection Steam Flow | 0 | lb/hr | CO | Carbone Monoxide | 0 | %
Temperature | 200 | F | CO2 | Carbon Dioxide | 0.632 | %
Pressure | 150 | Psig | H2O | Water | 0 | %
Phasa 0-water / 1-Steam | 0 |  | H2S | Hydrogen sulfide | 0 | %
|  |  | H2 | Hydrogen | 0 | %
Comprresor Extraction Air | 0 | lb/hr | He | Helium | 0 | %
Extraction Air Temperature | 600 | F | O2 | Oxygen | 0 | %
|  |  | Ar | Argon | 0 | %
Ref Temperature for Enthalpy | 80 | F
Exhaust Outlet Temperature | 1058 | F |  | RESULT
Generator |  |  |  | Fraction of Dry air | 0.95938
GT Power Output | 158.637 | MW |  | Humidity Ratio | 0.026334 | lb h2O/lb dry air
Generator Loss | 0 | MW | [11 empty] | in | 1611.2968 | MMBtu/h
Gearbox Loss | 0 | MW |  | Fuel LHV | 20822.5632 | BTU/lb | 11575.8251 | kcal/kg | [5 empty] | out | #NAME? | MMBtu/h
Fixed Head Loss | 0 | MMBtu/h |  | GT Exhaust Flow | #NAME? | lb/h | #NAME? | Ton/h | [5 empty] | eff | #NAME? | %
Variable Heat Loss | 0 | MMBtu/h |  | GT Exhaust Enthalpy | #NAME? | Btu/lb | #NAME? | kJ/kg
RESULT |  |  |  | SUMARRY | Flow lb/h | Enthalpy Btu/lb | Duty MMBtu/h
FUEL LHV | 20822.5632 | BTU/lb |  | Excess Air at Comp Inlet | #NAME? |  |  |  | Wet Exh Mole Fraction |  |  | Dry Exh Mole Fraction
molar flow change of 02 | 9315.1738 | mol/h |  | Combustion Air + Extr Fuel | #NAME? | 0 | #NAME? |  | N2 | #NAME? | % | N2 | #NAME? | %
molecular weight of dry air | 28.9651 | lb/lbmol |  | Fuel Gas | 77382.25 | 20822.5632 | 1611.2968 |  | O2 | #NAME? | % | O2 | #NAME? | %
O2 mole fraction of dry air | 0.20948 |  |  | Steam / Water Injection* | 0 | #NAME? | #NAME? |  | CO2 | #NAME? | % | CO2 | #NAME? | %
dry air to combustion | 1288050.5243 | lb/h |  | Compressor Extraction | 0 | #NAME? | #NAME? |  | H2O | #NAME? | % | Ar | #NAME? | %
spesific humidity | 0.026334 | lbwater/lbdryair | [6 empty] | Ar | #NAME? | % | SO2 | 0 | %
moist air to combustor | #NAME? | lb/h |  | Comb Prod at Turbine Exit | #NAME? | #NAME? | #NAME? |  | SO2 | #NAME? | %
total inlet air | #NAME? | lb/h |  | Power (MW*3.4121412) |  |  | -541.2918
compressor bleed air | 0 | lb/h |  | Total Heat Losss |  |  | 0
wet excess air | #NAME? | lb/h
wet combustion air | #NAME? | lb/h |  | Total Balance of Moist Air heat |  |  | #NAME?
|  |  |  | Change in Bal of Air Enthalpy |  | #NAME?
fuel flow | 77382.25 | lb/h |  | Balance of AirFlow | #NAME?
injection flow | 0 | lb/h
total combustor flow | #NAME? | lb/h | [10 empty] | 190600 | kg/h
|  |  |  | Change in Excess Air | #NAME? | #NAME? | #NAME? | [5 empty] | 130.4 | bar
turbine exhaust flow | #NAME? | lb/h |  | Excess Air at Turbine Exit | #NAME? | #NAME? | #NAME? | [5 empty] | 557.8 | C
[13 empty] | #NAME? | kJ/kg
|  |  |  | TURBINE EXHAUST | #NAME? | #NAME? | #NAME? | [5 empty] | #NAME? | kJ/h
[13 empty] | #NAME? | Mjoule/h
[13 empty] | #NAME? | MJ/s
[13 empty] | #NAME? | MW
[5 empty] | 80.6 | F
Methane | 91.026 | % |  |  | 77.3822 | klb/h
Ethane | 6.533 | %
Propane | 1.1 | % |  |  | 27 | C |  |  |  | input |  |  | output
I-Butane | 0.081 | % |  |  | 35.1 | Ton/h
N-Butane | 0.08 | % | 14.663 | Psia | [5 empty] | 35099.9695 | kg/h |  | #NAME? | kg/h
I-Petane | 0.027 | % | 88.682 | F | [5 empty] | 11575.8251 | kcal/kg
N-Petane | 0.022 | % | #NAME? | klb/h | [5 empty] | 48433.2521 | kJ/kg |  | #NAME? | KJ/kg
Hexane | 0 | % | [7 empty] | 1700005674.5475 | kJ/h |  | #NAME? | kJ/h
Nitrogen | 0.499 | % | 1010.9803 | mBar | [5 empty] | 1700005.6745 | MJ/h |  | #NAME? | MJ/h
Carbone Monoxide | 0 | % | 31.49 | C | [5 empty] | 472.2238 | MJ/s |  | #NAME? | MJ/s
Carbon Dioxide | 0.632 | % | #NAME? | Ton/h | [5 empty] | 472.2238 | MW |  | #NAME? | MW
Water | 0 | % | [7 empty] | 60 | % |  | 60 | %
Hydrogen sulfide | 0 | % |  |  |  |  | Gas |  |  | 283.3343 | MW |  | #NAME? | MW
Hydrogen | 0 | % |  |  |  |  | Turbine
Helium | 0 | % |  |  |  |  | 1058 | F
Oxygen | 0 | % |  |  |  |  | #NAME? | klb/h |  | #NAME?
Argon | 0 | % |  |  |  |  | #NAME? | Btu/lb
Fuel Gas LHV | 20822.5632 | BTU/lb |  |  |  |  | 570 | F
| 11575.8251 | kcal/kg |  |  |  |  | #NAME? | Ton/h
| 48465.6644 | kJ/kg |  |  |  |  | #NAME? | kJ/kg
Air Compressor
Gas
Turbine
Combustion

## ASME PTC 22
ASME PTC 22-2005 Table 4-4.5 (ISO 6976:1995 table 1)
Gas Properties Molar Mass for Component of Natural Gases at 60 F and 14.696 psia
Component | Formula | Molecular Weight lb/lbmol | Standard Density lb/1000ft3 | Heating Value (Dry),Btu/lb
|  |  |  | High | Low
Methane | CH4 | 16.0425 | 42.274 | 23892.2 | 21511.9 |  |  | CH4 | Methane
Ethane | C2H6 | 30.069 | 79.237 | 22334.1 | 20429.2 |  |  | C2H6 | Ethane
Propane | C3H8 | 44.0956 | 116.199 | 21654.1 | 19922.2 |  |  | C3H8 | Propane
I-Butane | i-C4H10 | 58.1222 | 153.161 | 21232.3 | 19589.8 |  |  | i-C4H10 | I-Butane
N-Butane | n-C4H10 | 58.1222 | 153.161 | 21300.2 | 19657.8 |  |  | n-C4H10 | N-Butane
I-Petane | i-C5H12 | 72.1488 | 190.123 | 21043.7 | 19455.9 |  |  | i-C5H12 | I-Petane
N-Petane | n-C5H12 | 72.1488 | 190.123 | 21085 | 19497.2 |  |  | n-C5H12 | N-Petane
Hexane | C6H14 | 86.1754 | 227.085 | 20943.8 | 19392.9 |  |  | C6H14 | Hexane
Heptane | C7H16 | 100.2019 | 264.048 | 20839.1 | 19314.7 |  |  | C7H16 | Heptane
n-Octane | C8H18 | 114.2285 | 301.01 | 20759.7 | 19255.4 |  |  | C8H18 | n-Octane
n-nonane | C9H20 | 128.2551 | 337.972 | 20701 | 19212.3 |  |  | C9H20 | n-nonane
n-decane | C10H22 | 142.2817 | 374.934 | 20651.6 | 19175.5 |  |  | C10H22 | n-decane
Carbone Monoxide | CO | 28.0101 | 73.811 | 4342.2 | 4342.2 |  |  | CO | Carbone Monoxide
Carbon Dioxide | CO2 | 44.0095 | 115.972 | 0 | 0 |  |  | CO2 | Carbon Dioxide
Hydrogen Sulfide | H2S | 34.0809 | 89.808 | 7094.1 | 6533.8 |  |  | H2S | Hydrogen Sulfide
Air | Air | 28.9651 | 76.328 | 0 | 0 |  |  | Air | Air
Hydrogen | H2 | 2.0159 | 5.321 | 61022.3 | 51566.7 |  |  | H2 | Hydrogen
Oxygen | O2 | 31.9988 | 84.322 | 0 | 0 |  |  | O2 | Oxygen
Nitrogen | N2 | 28.0134 | 73.82 | 0 | 0 |  |  | N2 | Nitrogen
Water | H2O | 18.0153 | 47.473 | 1059.8 | 0 |  |  | H2O | Water
Helium | He | 4.0026 | 10.547 | 0 | 0 |  |  | He | Helium
Argon | Ar | 39.948 | 105.269 | 0 | 0 |  |  | Ar | Argon
(ISO 6976:1995 table 3)
Calorific Value for component of natural gases for Natural Gases on a molar basis
Component | Ideal Calorific value on a molar basis (kJ-mol)
| 25 °C |  | 20 °C |  | 15 °C |  | 0 °C
| Superior | inferior | Superior | inferior | Superior | inferior | Superior | inferior
Methane |  |  |  |  | 891.56 | 802.69
Ethane |  |  |  |  | 1562.14 | 1428.84
Propane |  |  |  |  | 2221.1 | 2043.37
I-Butane |  |  |  |  | 2870.58 | 2648.42
N-Butane |  |  |  |  | 2879.76 | 2657.6
I-Petane |  |  |  |  | 3377.75 | 3155.59
N-Petane |  |  |  |  | 3538.6 | 3272
Hexane |  |  |  |  | 4198.24 | 3887.21
Heptane |  |  |  |  | 4857.18 | 4501.72
n-Octane |  |  |  |  | 5516.01 | 5116.11
n-nonane |  |  |  |  | 6175.82 | 5731.49
n-decane |  |  |  |  | 6834.9 | 6346.14
Carbone Monoxide |  |  |  |  | 282.91 | 282.91
Hydrogen Sulfide |  |  |  |  | 562.38 | 517.95
Hydrogen |  |  |  |  | 286.15 | 241.72
Water |  |  |  |  | 44.433 | 0
Component | Formula | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | ΔfH° | MW
Methane | CH4 | -176685.0998 | 2786.181 | -12.0258 | 0.039176 | -3.619e-05 | 2.0269e-08 | -4.9767e-12 | -23313.1436 | -74600 | 16.0425
Ethane | C2H6 | -186204.4161 | 3406.1919 | -19.5171 | 0.075658 | -8.2042e-05 | 5.0611e-08 | -1.3193e-11 | -27029.3289 | -83851.544 | 30.069
Propane | C3H8 | -243314.4337 | 4656.2708 | -29.3947 | 0.1189 | -0.00013763 | 8.8148e-08 | -2.343e-11 | -35403.3527 | -104680 | 44.0956
I-Butane | i-C4H10 | -383446.933 | 7000.0396 | -44.4003 | 0.17462 | -0.00020782 | 1.3398e-07 | -3.5517e-11 | -50340.1889 | -134990 | 58.1222
N-Butane | n-C4H10 | -317587.254 | 6176.3318 | -38.9156 | 0.15847 | -0.000186 | 1.1997e-07 | -3.2017e-11 | -45403.6339 | -125790 | 58.1222
I-Petane | i-C5H12 | -423190.339 | 6497.1891 | -36.8113 | 0.15324 | -0.00015488 | 8.7499e-08 | -2.0705e-11 | -51554.1659 | -153700 | 72.1488
N-Petane | n-C5H12 | -276889.4625 | 5834.2835 | -36.1754 | 0.15333 | -0.00015284 | 8.1911e-08 | -1.7923e-11 | -46653.7525 | -146760 | 72.1488
Hexane | C6H14 | -581592.67 | 10790.9772 | -66.3395 | 0.25237 | -0.00029043 | 1.8022e-07 | -4.6172e-11 | -72715.4457 | -166920 | 86.1754
Nitrogen | N2 | 22103.715 | -381.8462 | 6.0827 | -0.0085309 | 1.3847e-05 | -9.6258e-09 | 2.5197e-12 | 710.8461 | 0 | 28.0134
Carbone Monoxide | CO | 14890.4533 | -292.2286 | 5.7245 | -0.0081762 | 1.4569e-05 | -1.0877e-08 | 3.0279e-12 | -13031.3188 | -110535.196 | 28.0101
Carbon Dioxide | CO2 | 49436.5054 | -626.4116 | 5.3017 | 0.0025038 | -2.1273e-07 | -7.69e-10 | 2.8499e-13 | -45281.9846 | -393510 | 44.0095
Water | H2O | -39479.6083 | 575.5731 | 0.93178 | 0.0072227 | -7.3426e-06 | 4.955e-09 | -1.3369e-12 | -33039.7431 | -241826 | 18.0153
Hydrogen Sulfide | H2S | 9543.8088 | -68.7518 | 4.0549 | -0.00030146 | 3.7685e-06 | -2.2394e-09 | 3.0869e-13 | -3278.4573 | -20600 | 34.0809
Hydrogen Sulfide | H2S | 40783.2321 | -800.9186 | 8.2147 | -0.012697 | 1.7536e-05 | -1.2029e-08 | 3.3681e-12 | 2682.4847 | 0 | 34.0809
Helium | He | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | -745.375 | 0 | 4.0026
Oxygen | O2 | -34255.6342 | 484.7001 | 1.119 | 0.0042939 | -6.8363e-07 | -2.0234e-09 | 1.039e-12 | -3391.4549 | 0 | 31.9988
Argon | Ar | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | -745.375 | 0 | 39.948
C | 12011
H | 1007.94
O | 15999.4
N | 14006.74
S | 32066
Table B.2 - Molar Composition of dry air ISO 6976 ( ASME PTC 22-2005 A-3.2.1.3
Species | Molar Fraction
Nitrogen | 0.78102
Oxygen | 0.20946
Argon | 0.00916
Carbon dioxide | 0.00033
Neon | 1.82e-05
Helium | 5.2e-06
Methane | 1.5e-06
Krypton | 1.1e-06
Hydrogen | 5e-07
Dinitrogen Monoxide | 3e-07
Carbon Monoxide | 2e-07
Xenon | 1e-07
Table A-1 Element Molecular Weights ASME PTC22 2005
Nitrogen | 14.0067 | 75.7009 | 28.0134 | N2 | 2120.6407 |  | 1667.3624
Oxygen | 15.9994 | 20.3083 | 31.9988 | O2 | 649.8411 |  | 1904.574
Argon | 39.948 | 0.90792 | 39.948 | Ar | 36.2695 |  | 4755.4236
Carbon | 12.0107 | 0.030926 | 44.0095 | CO2 | 1.3611 |  | 1429.7578
Hydrogen | 1.0079 | 3.0519 | 18.0153 | H2O | 54.9812 |  | 119.9855
Sulfur | 32.065 | 0 A6: 3817.0286
Helium | 4.0026 | 44.433 A4: 28.6309; 0 A6: 476.4711
119.0403
| 548.352 | A1: rankine
| C1 | A1: -10214.165; A3: -10440.397
| C2 | A1: -4.8932; A3: -11.2946
| C3 | A1: -0.0053766; A3: -0.027022 |  | e= | 2.7183
| C4 | A1: 1.9202e-07; A3: 1.289e-05
| C5 | A1: 3.5576e-10; A3: -2.4781e-09
| C6 | A1: -9.0345e-14; A3: 0
| C7 | A1: 4.1635; A3: 6.546
| Vapor Press | A1: 0.90354; A3: 0.67051; 44.433 A4: psia
|  | T < 32 F |  | T > 32 F
INPUT SHEET |  | 0 A5: LABORATORIUM
Barometric Pressure | 14.663 | Psia |  |  |  | CH4 | Methane | 0.91026 | %
Inlet Dry Bulb Temperature | 88.682 | F |  |  |  | C2H6 | Ethane | 0.06533 | %
Inlet Wet Bulb Temperature | 0 | F |  |  |  | C3H8 | Propane | 0.011 | %
Inlet Relative Humidity | 88.83 | % |  |  |  | i-C4H10 | I-Butane | 0.00081 | %
[6 empty] | n-C4H10 | N-Butane | 0.0008 | %
GAS TURBINE COMPOSITION |  | 0 A5: i-C5H12; 0 A6: I-Petane; 0 A7: 0.00027; 0 A8: %
[6 empty] | n-C5H12 | N-Petane | 0.00022 | %
Injection Steam Flow | 0 | lb/hr | GT Fuel Flow | 77382.25 | lb/hr | C6H14 | Hexane | 0 | %
(Zero Standart) Temperature | 200 | F | Fuel Temperature | 80.6 | F | N2 | Nitrogen | 0.00499 | %
Pressure | 150 | Psig | Fuel LHV | 20822.5632 | Btu/lb | CO | Carbone Monoxide | 0 | %
Phasa 0-water / 1-Steam | 0 | 0 A5: CO2; 0 A6: Carbon Dioxide; 0 A7: 0.00632; 0 A8: %
|  |  | GT Power Output | 158.637 | MW | H2O | Water | 0 | %
Comprresor Extraction Air | 0 | lb/hr | Generator Loss | 0 | MW | H2S | Hydrogen sulfide | 0 | %
Extraction Air Temperature | 600 | F | Gearbox Loss | 0 | MW | H2 | Hydrogen | 0 | %
|  |  | Fixed Head Loss | 0 | MMBtu/h | He | Helium | 0 | %
Ref Temperature for Enthalpy | 80 | F | Variable Heat Loss | 0 | MMBtu/h | O2 | Oxygen | 0 | %
Exhaust Outlet Temperature | 1058 | F |  |  |  | Ar | Argon | 0 | %
GT EXHAUST FLOW | #NAME? | lb/h | #NAME? | kg/h |  |  | SUM | 100 | %
GT EXHAUST ENERGY | #NAME? | A1: MMBtu/h; A2: #NAME?; A3: kJ/kg
SUMMARY
| Flow lb/h | A1: Enthalpy Btu/lb; A2: Duty MMBtu/h
Excess Air at Comp Inlet | #NAME? | 44.433 A4: Wet Exh Mole Fraction
[5 empty] | N2 | #NAME? | %
Combustion Air + Extr Fuel | #NAME? | 0 | #NAME? |  | O2 | #NAME? | %
Fuel Gas | 77382.25 | 20822.5632 | 1611.2968 |  | CO2 | #NAME? | %
Steam / Water Injection* | 0 | #NAME? | #NAME? |  | H2O | #NAME? | %
Compressor Extraction | 0 | #NAME? | #NAME? |  | Ar | #NAME? | %
[5 empty] | SO2 | #NAME? | %
Comb Prod at Turbine Exit | #NAME? | A1: #NAME?; A2: #NAME?
Dry Exh Mole Fraction
Power (MW*3.4121412) |  | A2: -541.2918; 44.433 A4: N2; 0 A5: #NAME?; 0 A6: %
Total Heat Losss |  | A2: 0; 44.433 A4: O2; 0 A5: #NAME?; 0 A6: %
[5 empty] | CO2 | #NAME? | %
Total Balance of Moist Air Heat |  | A2: #NAME?; 44.433 A4: Ar; 0 A5: #NAME?; 0 A6: %
Change in Bal of Air Enthalpy |  | A1: #NAME?; 44.433 A4: SO2; 0 A5: 0; 0 A6: %
Balance of AirFlow | #NAME?
Change in Excess Air | #NAME? | A1: #NAME?; A2: #NAME?
Excess Air at Turbine Exit | #NAME? | A1: #NAME?; A2: #NAME?
Turbine Exhaust | #NAME? | A1: #NAME?; A2: #NAME?
Ambient Condition
Patm | Ambient Pressure | A1: psia; A2: 14.663; A3: inputan
| Ambient Temperature | A1: °F; A2: 88.682
| Ambient Humidity | A1: %; A2: 88.83
Humidity Calculation
| Vapor Pressure | A1: psia; A2: 0.67051; A3: variable
pH2O | Partial Pressuure | A1: psia; A2: 0.59561
FDA | Fraction of dry air | A1: -; A2: 0.95938
| Humidity ratio | A1: lb h2O/lb dry air; A2: 0.026334
| Moist air flow | lb/h | #NAME? | #NAME? | kg/h | #NAME? | kg/s | anakan
| Excess air | lb/h | #NAME? | #NAME? | kg/h | #NAME? | kg/s
Moisture Air to Combustor
A1 | A2 | A3 | A4 | A5 | A6 | A7
Compound | formula | air mole fraction wet [ MFi ] | molecular weight [ MWi ] | A3 X A4 | moist air molar flow to comb lb/h x (A3)/sum(A5) =mol/h [ Mi ] | Air weight fraction (A5)/sum(A5) [ mFi ]
N2 | 0.780840 x FDA | 0.74912 | 28.0134 | 20.9855 | #NAME? | 0.73581
O2 | 0.209476 x FDA | 0.20097 | 31.9988 | 6.4307 | #NAME? | 0.22548 | anakan
CO2 | 0.000319 x FDA | 0.00030604 | 44.0095 | 0.013469 | #NAME? | 0.00047225
H2O | 1-FDA | 0.04062 | 18.0153 | 0.73178 | #NAME? | 0.025658
Ar | 0.009365 x FDA | 0.0089846 | 39.948 | 0.35892 | #NAME? | 0.012585
| average molecular weight [ MW wet air] |  |  | 28.5203 | kg/mol
Dry Air to Combustor
A1 | A8 | A9 | A10 | g
Compound | air mole fraction dry | molecular weight | (A8) x (A9)
N2 | 0.78084 | 28.0134 | 21.874 | #NAME?
O2 | 0.20948 | 31.9988 | 6.703 | #NAME?
CO2 | 0.000319 | 44.0095 | 0.014039 | #NAME?
H2O |  | 18.0153 | 0 | #NAME?
Ar | 0.009365 | 39.948 | 0.37411 | #NAME?
| average molecular weight [ MW dry air] |  | 28.9651 | #NAME?
Excess Air
A1 | A11 | A12 | A13 | A14 | A15 | A16
Compound | Formula | air mole fraction | molecular weight | A12 x A13 | excess moist air molar flow lb/h x (A12)/sum(14) = mol/h | Air Weight Fraction [A14/Sum[A14]
N2 | 0.780840 x FDA | 0.74912 | 28.0134 | 20.9855 | #NAME? | 0.73581
O2 | 0.209476 x FDA | 0.20097 | 31.9988 | 6.4307 | #NAME? | 0.22548
CO2 | 0.000319 x FDA | 0.00030604 | 44.0095 | 0.013469 | #NAME? | 0.00047225
H2O | 1-FDA | 0.04062 | 18.0153 | 0.73178 | #NAME? | 0.025658
Ar | 0.009365 x FDA | 0.0089846 | 39.948 | 0.35892 | #NAME? | 0.012585
|  | average molecular weight [ MW dry air] |  | 28.5203
MASS FLOW CALCULATIONS
molar flow change of 02 | 9315.1738 | mol/h
molecular weight of dry air | 28.9651 | lb/lbmol
O2 mole fraction of dry air | 0.20948
dry air to combustion | 1288050.5243 | lb/h
spesific humidity | 0.026334 | lbwater/lbdryair
moist air to combustor | #NAME? | lb/h
total inlet air | #NAME? | lb/h | #NAME? | kg/h
compressor bleed air | 0 | lb/h | 0 | kg/h
wet excess air | #NAME? | lb/h | #NAME? | kg/h
wet combustion air | #NAME? | lb/h | #NAME? | kg/h
fuel flow | 77382.25 | lb/h | ` | kg/h
injection flow | 0 | lb/h | 0 | kg/h
total combustor flow | #NAME? | lb/h | #NAME? | kg/h
turbine exhaust flo | #NAME? | lb/h | #NAME? | kg/h
FUEL GAS COMBUSTION CALCULATION
Fuel Gas Mass Flow | 77382.25 | lb/h
Fuel Gas Molar Flow | 4396.9365 | mol/h
|  | C2 | C3 | C4 | C5 | C6 | C7 | C8 | C9 | C10 | C11 | C12 | C13 | C14 | C15 | C16
Symbol | Description | Mole Fraction | Molecular weight | Molar flow A2 x A3 | N2 ratio | N2 mole change mol/h x C2 x C5 | O2 ratio | O2 mole change mol/h x C2 x C7 | CO2 ratio | CO2 mole change mol/h x C2 x C9 | H2O ratio | H2O mole change mol/h x C2 x C11 | Ar ratio | Ar mole change mol/h x C2 x C13 | SO2 ratio | Ar mole change mol/h x C2 x C15
CH4 | Methane | 0.91026 | 16.0425 | 14.6028 | 0 | 0 | -2 | -8004.7108 | 1 | 4002.3554 | 2 | 8004.7108 | 0 | 0 | 0 | 0
C2H6 | Ethane | 0.06533 | 30.069 | 1.9644 | 0 | 0 | -3.5 | -1005.3815 | 2 | 574.5037 | 3 | 861.7556 | 0 | 0 | 0 | 0
C3H8 | Propane | 0.011 | 44.0956 | 0.48505 | 0 | 0 | -5 | -241.8315 | 3 | 145.0989 | 4 | 193.4652 | 0 | 0 | 0 | 0
i-C4H10 | I-Butane | 0.00081 | 58.1222 | 0.047079 | 0 | 0 | -6.5 | -23.1499 | 4 | 14.2461 | 5 | 17.8076 | 0 | 0 | 0 | 0
n-C4H10 | N-Butane | 0.0008 | 58.1222 | 0.046498 | 0 | 0 | -6.5 | -22.8641 | 4 | 14.0702 | 5 | 17.5877 | 0 | 0 | 0 | 0
i-C5H12 | I-Petane | 0.00027 | 72.1488 | 0.01948 | 0 | 0 | -8 | -9.4974 | 5 | 5.9359 | 6 | 7.123 | 0 | 0 | 0 | 0
n-C5H12 | N-Petane | 0.00022 | 72.1488 | 0.015873 | 0 | 0 | -8 | -7.7386 | 5 | 4.8366 | 6 | 5.804 | 0 | 0 | 0 | 0
C6H14 | Hexane | 0 | 86.1754 | 0 | 0 | 0 | -9.5 | 0 | 6 | 0 | 7 | 0 | 0 | 0 | 0 | 0
N2 | Nitrogen | 0.00499 | 28.0134 | 0.13979 | 1 | 21.9407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
CO | Carbone Monoxide | 0 | 28.0101 | 0 | 0 | 0 | -0.5 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 0
CO2 | Carbon Dioxide | 0.00632 | 44.0095 | 0.27814 | 0 | 0 | 0 | 0 | 1 | 27.7886 | 0 | 0 | 0 | 0 |  | 0
H2O | Water | 0 | 18.0153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0
H2S | Hydrogen sulfide | 0 | 34.0809 | 0 | 0 | 0 | -1.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0
H2 | Hydrogen | 0 | 2.0159 | 0 | 0 | 0 | -0.5 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  | 0
He | Helium | 0 | 4.0026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0
O2 | Oxygen | 0 | 31.9988 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
Ar | Argon | 0 | 39.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 |  | 0
C7H16 | Heptane | 0 | 100.2019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | average molar weight |  | 17.5991
|  | Molar flow change |  |  |  | 21.9407 |  | -9315.1738 |  | 4788.8355 |  | 9108.254 |  | 0 |  | 0
water or steam injec flow | 0 | mol/h C2: lb/h; mol/h C3: 0; mol/h C4: kg/h
GT Fuel Flow | 77382.25 | mol/h C2: lb/h; mol/h C3: 35099.9695; mol/h C4: kg/h
Moist Air to Comb | #NAME? | mol/h C2: lb/h; mol/h C3: #NAME?; mol/h C4: kg/h
Total Comb flow | #NAME? | mol/h C2: lb/h; mol/h C3: #NAME?; mol/h C4: kg/h
Excess Air flow | #NAME? | mol/h C2: lb/h; mol/h C3: #NAME?; mol/h C4: kg/h
Turbine Exhaust flow | #NAME? | mol/h C2: lb/h; mol/h C3: #NAME?; mol/h C4: kg/h
Combustion Product
E1 | E2 | E3 | E4 | E5 | E6 | E7 | E9 | E8
Compound | Air Molar Flow [A6] | Combustion Mole Change | Wt or stm inj Molar Flow lb/h [E7] | Comb Exh Molar Flow [E2]+[E3]+[E4] | Comb Exh Mole Fraction [E5]/Sum[E5] | Molecular Weight | Comb Exhaust Mass Fraction [E5] x [E7]/Comb Flow
N2 | #NAME? | 21.9407 | 0 | #NAME? | #NAME? | 28.0134 | #NAME? | #NAME?
O2 | #NAME? | -9315.1738 | 0 | 0 | #NAME? | 31.9988 | #NAME? | 0
CO2 | #NAME? | 4788.8355 | 0 | #NAME? | #NAME? | 44.0095 | #NAME? | #NAME?
H2O | #NAME? | 9108.254 | 0 | #NAME? | #NAME? | 18.0153 | #NAME? | #NAME?
Ar | #NAME? | 0 | 0 | #NAME? | #NAME? | 39.948 | #NAME? | #NAME?
SO2 | 0 | 0 | 0 | 0 | #NAME? | 64.0638 | #NAME? | 0
|  |  | sum = | #NAME? |  | 226.0488 | #NAME? | #NAME?
Turbine Exhaust
E1 | E10 | E11 | E12 | E13 | E14
Compound | Excess Air Molar Flow [A15] | Turbine Exhaust Molar Flow [E5]+[E10] | Wet Exhaust mole fraction [E11]/wetsum[E11] | Dry Exhaust mole fraction [E11]/wetsum[E11] | wet Turbine Exh mole fraction [E11]x[E7]/TEF
N2 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
O2 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
CO2 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
H2O | #NAME? | #NAME? | #NAME? |  | #NAME?
Ar | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
SO2 | 0 | 0 | #NAME? | 0
#NAME?
| wet sum | #NAME? | #NAME? | #NAME? | #NAME?
| dry sum | #NAME?
COMBUSTION PRODUCT AT TURBINE EXIT ENTHALPY
EXHAUST TEMPERATURE | 1058 | F |  |  | Reff Temperature | 80 | F
Turbine Exhaust E10: 843.15; Turbine Exhaust E11: K | 299.8167 | K
F1 | F2 | F3 | F4 |  | F1 | F2 | F3 | F4
Compound |  |  |  |  | Compound
N2 | #NAME? | 251.824 | #NAME? |  | N2 | #NAME? | 0.74501 | #NAME?
O2 | #NAME? | 232.4409 | #NAME? |  | O2 | #NAME? | 0.65795 | #NAME?
CO2 | #NAME? | 244.6459 | #NAME? |  | CO2 | #NAME? | 0.60524 | #NAME?
H2O | #NAME? | 469.7884 | #NAME? |  | H2O | #NAME? | 1.336 | #NAME?
Ar | #NAME? | 121.9182 | #NAME? |  | Ar | #NAME? | 0.37284 | #NAME?
SO2 | #NAME? | 174.0769 | #NAME? |  | SO2 | #NAME? | 0.44595 | #NAME?
Turbine Exhaust E11: Exh Enthalpy; Turbine Exhaust E12: #NAME?; Turbine Exhaust E13: Btu/lb |  | Exh Enthalpy | #NAME? | Btu/lb |  |  | #NAME?
[7 empty] | Enthalpy at Process Temp | #NAME? | Btu/lb
#NAME?
MOISTURE AIR ENTHALPY
Inlet Air Temp | 88.682 | F |  |  | Extraction Air Temp | 600 | F |  |  | Exhaust Gas Temp | 1058 | F
Turbine Exhaust E10: 304.64; Turbine Exhaust E11: K; Turbine Exhaust E12: MAX = 1000 K | 588.7056 | K |  |  |  | 843.15 | K
G1 | G2 | G3 | G4 |  | G1 | G2 | G3 | G4 |  | G1 | G2 | G3 | G4
Turbine Exhaust E1: Compound; Turbine Exhaust E14: Compound |  |  |  |  | Compound
N2 | 0.73581 | #NAME? | #NAME? |  | N2 | 0.73581 | 131.2839 | 96.5996 |  | N2 | 0.73581 | 251.824 | 185.2939
O2 | 0.22548 | 2.5631 | 0.57793 |  | O2 | 0.22548 | 119.3513 | 26.9111 |  | O2 | 0.22548 | 232.4409 | 52.4103
CO2 | 0.00047225 | 2.3638 | 0.0011163 |  | CO2 | 0.00047225 | 120.8962 | 0.057093 |  | CO2 | 0.00047225 | 244.6459 | 0.11553
H2O | 0.025658 | 5.2043 | 0.13353 |  | H2O | 0.025658 | 240.8353 | 6.1794 |  | H2O | 0.025658 | 469.7884 | 12.0539
Ar | 0.012585 | 1.4518 | 0.018271 |  | Ar | 0.012585 | 64.9982 | 0.81797 |  | Ar | 0.012585 | 121.9182 | 1.5343
SO2 | 0 | 1.7404 | 0 |  | SO2 | 0 | 87.0353 | 0 |  | SO2 | 0 | 174.0769 | 0
Turbine Exhaust E11: Exh Enthalpy; Turbine Exhaust E12: #NAME?; Turbine Exhaust E13: Btu/lb |  | Exh Enthalpy | 130.5652 | Btu/lb |  |  | Exh Enthalpy | 251.4079 | Btu/lb
[8 empty] | #NAME? |  |  |  |  | #NAME? | Btu/lb
TURBINE EXHAUST EXCESS AIR | 1058 | F |  |  | Reff Temperature | 80 | F
Turbine Exhaust E10: 843.15; Turbine Exhaust E11: K | 299.8167 | K
F1 | F2 | F3 | F4 |  | F1 | F2 | F3 | F4
Compound |  |  |  |  | Compound
N2 | #NAME? | 251.824 | #NAME? |  | N2 | #NAME? | 0.74501 | #NAME?
O2 | #NAME? | 232.4409 | #NAME? |  | O2 | #NAME? | 0.65795 | #NAME?
CO2 | #NAME? | 244.6459 | #NAME? |  | CO2 | #NAME? | 0.60524 | #NAME? |  | 84.6
H2O | #NAME? | 469.7884 | #NAME? |  | H2O | #NAME? | 1.336 | #NAME? |  | 2.326
Ar | #NAME? | 121.9182 | #NAME? |  | Ar | #NAME? | 0.37284 | #NAME? |  | 36.3715
SO2 | 0 | 174.0769 | 0 |  | SO2 | 0 | 0.44595 | 0
Turbine Exhaust E11: Enthalpy; Turbine Exhaust E12: #NAME?; Turbine Exhaust E13: Btu/lb |  | Exh Enthalpy | #NAME? | Btu/lb | #NAME?
[7 empty] | Enthalpy at Process Temp | #NAME? | Btu/lb
Constituent | A1 | A2 | A3 | A4 | A5 | A6 | A7 | A8 | ΔfH° | MW
N2 | 22103.715 | -381.8462 | 6.0827 | -0.0085309 | 1.3846e-05 | -9.6258e-09 | 2.5197e-12 | 710.8461 | 0 | 28.0134
O2 | -34255.6342 | 484.7001 | 1.119 | 0.0042939 | -6.8363e-07 | -2.0234e-09 | 1.039e-12 | -3391.4549 | 0 | 31.9988
CO2 | 49436.5054 | -626.4116 | 5.3017 | 0.0025038 | -2.1273e-07 | -7.69e-10 | 2.8497e-13 | -45281.9846 | -393510 | 44.0095
H2O | -39479.6083 | 575.5731 | 0.93178 | 0.0072227 | -7.3426e-06 | 4.955e-09 | -1.3369e-12 | -33039.7431 | -241826 | 18.0153
Ar | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | -745.375 | 0 | 39.948
SO2 | -53108.4214 | 909.0312 | -2.3569 | 0.022045 | -2.5108e-05 | 1.4463e-08 | -3.3691e-12 | -41137.5212 | -296810 | 64.0638
CALCULATION OF GAS SENSIBLE HEAT
Fuel Gas Temperature | 80.6 | F |  |  | Reff Temperature | 80 | F
| 300.15 | K |  |  |  | 299.8167 | K
| 540.27 | R |  |  |  | 539.67 | R
Symbol | Compound | Stream mass Fraction | Compound Enthalpy | [H2] x [H3] | Symbol | Compound | Stream mass Fraction | Compound Enthalpy | [H2] x [H3]
CH4 | Methane | 0.82975 | 1.9151 | 1.589 | CH4 | Methane | 0.82975 | 1.5956 | 1.324
C2H6 | Ethane | 0.11162 | 1.5048 | 0.16797 | C2H6 | Ethane | 0.11162 | 1.2535 | 0.13992
C3H8 | Propane | 0.027561 | 1.4387 | 0.039652 | C3H8 | Propane | 0.027561 | 1.1983 | 0.033028
i-C4H10 | I-Butane | 0.0026751 | 1.4335 | 0.0038346 | i-C4H10 | I-Butane | 0.0026751 | 1.1939 | 0.0031939
n-C4H10 | N-Butane | 0.002642 | 1.4633 | 0.0038662 | n-C4H10 | N-Butane | 0.002642 | 1.2189 | 0.0032205
i-C5H12 | I-Petane | 0.0011069 | 1.4207 | 0.0015725 | i-C5H12 | I-Petane | 0.0011069 | 1.1833 | 0.0013098
n-C5H12 | N-Petane | 0.0009019 | 1.4341 | 0.0012934 | n-C5H12 | N-Petane | 0.0009019 | 1.1946 | 0.0010774
C6H14 | Hexane | 0 | 1.4266 | 0 | C6H14 | Hexane | 0 | 1.1884 | 0
N2 | Nitrogen | 0.0079428 | 0.89401 | 0.0071009 | N2 | Nitrogen | 0.0079428 | 0.74501 | 0.0059175
CO | Carbone Monoxide | 0 | 0.89455 | 0 | CO | Carbone Monoxide | 0 | 0.74545 | 0
CO2 | Carbon Dioxide | 0.015804 | 0.72644 | 0.011481 | CO2 | Carbon Dioxide | 0.015804 | 0.60524 | 0.0095653
H2O | Water | 0 | 1.6033 | 0 | H2O | Water | 0 | 1.336 | 0
H2S | Hydrogen sulfide | 0 | 0.86454 | 0 | H2S | Hydrogen sulfide | 0 | 0.72041 | 0
H2 | Hydrogen | 0 | 0.72775 | 0 | H2 | Hydrogen | 0 | 0.60644 | 0
He | Helium | 0 | 4.4653 | 0 | He | Helium | 0 | 3.7211 | 0
O2 | Oxygen | 0 | 0.78956 | 0 | O2 | Oxygen | 0 | 0.65795 | 0
Ar | Argon | 0 | 0.44741 | 0 | Ar | Argon | 0 | 0.37284 | 0
| A3: Fuel Gas enthalpy; A4: 1.8258; #NAME? A8: Fuel Gas enthalpy | 1.5212
CALCULATION OF FUEL LHV
Fuel Gas Temperature | 80.6 | F | Refference Temperature |  | 80 | F
Symbol | Compound | Fuel Mole Fraction | Mol.wt | [J2]x[J3] | Fuel Wt.Fraction [J4]/Sum[J4] | Heat of Comb Btu/lb | [J5] x [J6] | Heat of Comb Btu/lb
CH4 | Methane | 0.91026 | 16.0425 | 14.6028 | 0.82975 | 21511.9 | 17849.417 | 23892.2 | 19824.4618
C2H6 | Ethane | 0.06533 | 30.069 | 1.9644 | 0.11162 | 20429.2 | 2280.3023 | 22334.1 | 2492.9267
C3H8 | Propane | 0.011 | 44.0956 | 0.48505 | 0.027561 | 19922.2 | 549.0783 | 21654.1 | 596.8114
i-C4H10 | I-Butane | 0.00081 | 58.1222 | 0.047079 | 0.0026751 | 19589.8 | 52.4042 | 21232.3 | 56.798
n-C4H10 | N-Butane | 0.0008 | 58.1222 | 0.046498 | 0.002642 | 19657.8 | 51.9369 | 21300.2 | 56.2762
i-C5H12 | I-Petane | 0.00027 | 72.1488 | 0.01948 | 0.0011069 | 19455.9 | 21.5354 | 21043.7 | 23.2929
n-C5H12 | N-Petane | 0.00022 | 72.1488 | 0.015873 | 0.0009019 | 19497.2 | 17.5846 | 21085 | 19.0167
C6H14 | Hexane | 0 | 86.1754 | 0 | 0 | 19392.9 | 0 | 20943.8 | 0
N2 | Nitrogen | 0.00499 | 28.0134 | 0.13979 | 0.0079428 | 0 | 0 | 0 | 0
CO | Carbone Monoxide | 0 | 28.0101 | 0 | 0 | 4342.2 | 0 | 4342.2 | 0
CO2 | Carbon Dioxide | 0.00632 | 44.0095 | 0.27814 | 0.015804 | 0 | 0 | 0 | 0
H2O | Water | 0 | 18.0153 | 0 | 0 | 0 | 0 | 1059.8 | 0
H2S | Hydrogen sulfide | 0 | 34.0809 | 0 | 0 | 6533.8 | 0 | 7094.1 | 0
H2 | Hydrogen | 0 | 2.0159 | 0 | 0 | 51566.7 | 0 | 61022.3 | 0
He | Helium | 0 | 4.0026 | 0 | 0 | 0 | 0 | 0 | 0
O2 | Oxygen | 0 | 31.9988 | 0 | 0 | 0 | 0 | 0 | 0
Ar | Argon | 0 | 39.948 | 0 | 0 | 0 | 0 | 0 | 0
C7H16 | Heptane | 0 | 100.2019 | 0 | 0 | 19314.7 | 0 | 20839.1 | 0
| A4: 17.5991; Enthalpy at Process Temp A7: 20822.2586 | 23069.5837
|  | LHV |  | HHV
Fuel Gas LHV | A2: 20822.2586; A3: Btu/lb; A4: 23069.5837; A5: Btu/lb
Spesific Enthalpy of Fuel at Proses Temp | A2: 1.8258; A3: Btu/lb; A4: 1.8258; A5: Btu/lb
Spesific Enthalpy of Fuel at Reff Temp | A2: 1.5212; A3: Btu/lb; A4: 1.5212; A5: Btu/lb
HV gas= LHV + SH Tfuel - SH Tref | A2: 20822.5632; A3: Btu/lb; A4: 23069.8883; A5: Btu/lb
|  | 11575.8251 | Kcal/kg | 12825.1738 | Kcal/kg